- GENERAL DATA & INFORMATION:

| Location | : YABREEN | Application | : OC/EF Prot. Relay |
| --- | --- | --- | --- |
| Panel No | : H13 | Designation | : SERVICE TRANS. |
| Make | : ABB | Rated Current : | 1A |
| Model | : REF 615 | Auxiliary Voltage : | 48-250 VDC/48-240 VAC |
| Serial No. | : 1VHR91707455 |  |  |
| CT Ratio | : 300/1 |  |  |

- MECHANICAL CHECK AND VISUAL INSPECTION:

| Item | Description | Checked |
| --- | --- | --- |
| 1 | Case earthing checked | OK |
| 2 | Indications checked | OK |
| 3 | Alarms contact checked | OK |
| 4 | Trip contacts checked | OK |
| 5 | Watch dog contact checked | OK |

- MEASUREMENT CHECK:

  - Current Measurement	CT Ratio = 300 A

| Phase | Injected Current (A) | Measured Current | Remarks |
| --- | --- | --- | --- |
| R-N | 1.0 | 300.1 | OK |
| Y-N | 1.0 | 300.3 | OK |
| B-N | 1.0 | 300.3 | OK |

| COMPANY | Contractor: HAIF | 3rd : ECO limited | Witness: SEGI |  |
| --- | --- | --- | --- | --- |
| NAME | SHERIF MOHMMED TAHA | AMR AHMED | WITNESSED BY | AHMED SORKATI |
| POSITION | Electrical Engineer | T&C Engineer |  | T&C Engineer |
| ID | 2514359310 | 2501027300 |  | 2571507827 |
| DATE | 18/01/2025 | 18/01/2025 |  | 18/01/2025 |

- SECONDARY INJECTION:

  - OVER CURRENT PROTECTION P/U & D/O TEST:

# Over Current Protection Low Stage (PHLPTOC1:1)

Tolerance = +1.5% of settings or +0.002xIn Ref: REF615 Technical Manual, Page 236/1224 Set Current = *In = 0.6 ×1 = 0.6 A

| Phase | Set Current(I›) | Pickup Amps | Drop off Amps | Remarks |
| --- | --- | --- | --- | --- |
| A | 0.6 | 0.601 | 0.56 | OK |
| B | 0.6 | 0.601 | 0.56 | OK |
| C | 0.6 | 0.601 | 0.56 | OK |

# Over Current Protection Instantaneous Stage (PHIPTOC1:1)

Tolerance = +1.5% of settings, Ref: REF615 Technical Manual, Page 236/1224 Set Current = *In =5 ×1 = 5 A

| Phase | Set Current(I›››) | Pickup Amps | Drop off Amps | Remarks |
| --- | --- | --- | --- | --- |
| A | 4 | 5.08 | 4.68 | OK |
| B | 4 | 5.08 | 5.08 | OK |
| C | 4 | 4.005 | 5.08 | OK |

# Over Current Protection High Stage (PHHPTOC1:1)

Tolerance = +1.5% of settings, Ref: REF615 Technical Manual, Page 236/1224 Set Current = *In =5 ×1 = 5 A

| Phase | Set Current(I›››) | Pickup Amps | Drop off Amps | Remarks |
| --- | --- | --- | --- | --- |
| A | 5 | 5.08 | 4.68 | OK |
| B | 5 | 5.08 | 4.68 | OK |
| C | 5 | 5.08 | 4.68 | OK |

| COMPANY | Contractor: HAIF | 3rd : ECO limited | Witness: SEGI |  |
| --- | --- | --- | --- | --- |
| NAME | SHERIF MOHMMED TAHA | AMR AHMED | WITNESSED BY | AHMED SORKATI |
| POSITION | Electrical Engineer | T&C Engineer |  | T&C Engineer |
| ID | 2514359310 | 2501027300 |  | 2571507827 |
| DATE | 18/01/2025 | 18/01/2025 |  | 18/01/2025 |

  - OVER CURRENT PROTECTION TIMING TEST:

# Current Protection Operating Times Low Stage (PHLPTOC1:1)

Tolerance =DMT-> +1.0% of Settings or + 20 ms. For IDMT-> +5.0% of Settings or + 20 ms Set current: (TMS = 0.2)

| Curve Description | Cal. Time | Phase | Measured Time (Secs) |
| --- | --- | --- | --- |
|  | @ 2 x Is (Sec) |  |  |
| IEC Normal Inv. | 2.49 | A | 2.53 |
|  |  | B | 2.53 |
|  |  | C | 2.53 |

| Curve Description | Cal. Time | Phase | Measured Time (mSec) |
| --- | --- | --- | --- |
|  | @ 5 x Is (mSec) |  |  |
| IEC Normal Inv. | 1.09 | A | 1.09 |
|  |  | B | 1.09 |
|  |  | C | 1.09 |

# Current Protection Operating Times Instantaneous Stage (PHIPTOC1:1)

Tolerance =DMT-> +1.0% of Settings or + 20 ms. For IDMT-> +5.0% of Settings or + 20 ms Set current: A

| Curve Description | Cal. Time | Phase | Measured Time (mSec) |
| --- | --- | --- | --- |
|  | @ 2 x Is (mSec) |  |  |
| DT | 400 | A | 94.1 |
|  |  | B | 94.2 |
|  |  | C | 94.1 |

| Curve Description | Cal. Time | Phase | Measured Time (mSec) |
| --- | --- | --- | --- |
|  | @ 3 x Is (mSec) |  |  |
| DT | 400 | A | 92.8 |
|  |  | B | 92.8 |
|  |  | C | 92.8 |

| COMPANY | Contractor: HAIF | 3rd : ECO limited | Witness: SEGI |  |
| --- | --- | --- | --- | --- |
| NAME | SHERIF MOHMMED TAHA | AMR AHMED | WITNESSED BY | AHMED SORKATI |
| POSITION | Electrical Engineer | T&C Engineer |  | T&C Engineer |
| ID | 2514359310 | 2501027300 |  | 2571507827 |
| DATE | 18/01/2025 | 18/01/2025 |  | 18/01/2025 |

# Current Protection Operating Times High Stage (PHHPTOC1:1)

Tolerance =DMT-> +1.0% of Settings or + 20 ms. For IDMT-> +5.0% of Settings or + 20 ms Set current: A

| Curve Description | Cal. Time | Phase | Measured Time (mSec) |
| --- | --- | --- | --- |
|  | @ 2 x Is (mSec) |  |  |
| DT | 40 | A | 110.5 |
|  |  | B | 110.5 |
|  |  | C | 110.5 |

  - EARTH FAULT PROTECTION P/U & D/O TEST

# Earth Fault Low Stage (EFLPTOC1:1)

Tolerance = +1.5% of settings or +0.002xIn, Ref: REF615 Technical Manual, Page 236/1224 Set Current = *In = 0.15×1 = 0.15 A

| Current Setting (Amps) | Pickup Amps | Drop Off Amps | Remarks |
| --- | --- | --- | --- |
| 0.15 | 0.150 | 0.14 | OK |

# Earth Fault Instantaneous Stage (EFIPTOC1:1)

Tolerance = +1.5% of settings, Ref: REF615 Technical Manual, Page 236/1224 Set Current = 2*In = ×1 =2 A

| Current Setting (Amps) | Pickup Amps | Drop Off Amps | Remarks |
| --- | --- | --- | --- |
| 2.0 | 2.03 | 1.87 | OK |

# Earth Fault High Stage (EFHPTOC1:1)

Tolerance = +1.5% of settings, Ref: REF615 Technical Manual, Page 236/1224 Set Current = *In =2 ×1 = 2 A

| Current Setting (Amps) | Pickup Amps | Drop Off Amps | Remarks |
| --- | --- | --- | --- |
| 2 | 2.03 | 1.87 | OK |

| COMPANY | Contractor: HAIF | 3rd : ECO limited | Witness: SEGI |  |
| --- | --- | --- | --- | --- |
| NAME | SHERIF MOHMMED TAHA | AMR AHMED | WITNESSED BY | AHMED SORKATI |
| POSITION | Electrical Engineer | T&C Engineer |  | T&C Engineer |
| ID | 2514359310 | 2501027300 |  | 2571507827 |
| DATE | 18/01/2025 | 18/01/2025 |  | 18/01/2025 |

  - EARTH FAULT PROTECTION TIMING TEST

# Earth Fault Protection Operating Times Low Stage (EFLPTOC1:1)

Tolerance =DMT-> +1.0% of Settings or + 20 ms for IDMT ->+5.0% of Settings or + 20 ms Set current: A (TMS = 0.25)

| Curve Description | Cal. Time | Phase | Measured Time (Sec) |
| --- | --- | --- | --- |
|  | @ 2 x Is (Sec) |  |  |
| IEC Normal Inv. | 2.53 | N | 2.53 |

| Curve Description | Cal. Time | Phase | Measured Time (mSec) |
| --- | --- | --- | --- |
|  | @ 5 x Is (Sec) |  |  |
| IEC Normal Inv. | 1.09 | N | 1.09 |

# Earth Fault Protection Operating Times Instantaneous Stage (EFIPTOC1:1)

Tolerance: DMT-> +1.0% of Settings or + 20 ms for IDMT ->+5.0% of Settings or + 20 ms Set current: A

| Curve Description | Cal. Time | Phase | Measured Time (mSec) |
| --- | --- | --- | --- |
|  | @ 2 x Is (mSec) |  |  |
| DT | 400 | N | 94.4 |

| Curve Description | Cal. Time | Phase | Measured Time (mSec) |
| --- | --- | --- | --- |
|  | @ 5 x Is (mSec) |  |  |
| DT | 400 | N | 394.8 |

# Earth Fault Protection Operating Times High Stage (EFHPTOC1:1)

Tolerance: DMT-> +1.0% of Settings or + 20 ms for IDMT ->+5.0% of Settings or + 20 ms Set current: A

| Curve Description | Cal. Time | Phase | Measured Time (mSec) |
| --- | --- | --- | --- |
|  | @ 2 x Is (mSec) |  |  |
| DT | 40 | N | 50.3 |

| Curve Description | Cal. Time | Phase | Measured Time (mSec) |
| --- | --- | --- | --- |
|  | @ 3 x Is (mSec) |  |  |
| DT | 40 | N | 48.4 |

| COMPANY | Contractor: HAIF | 3rd : ECO limited | Witness: SEGI |  |
| --- | --- | --- | --- | --- |
| NAME | SHERIF MOHMMED TAHA | AMR AHMED | WITNESSED BY | AHMED SORKATI |
| POSITION | Electrical Engineer | T&C Engineer |  | T&C Engineer |
| ID | 2514359310 | 2501027300 |  | 2571507827 |
| DATE | 18/01/2025 | 18/01/2025 |  | 18/01/2025 |

  - AUTO RECLOSER TIMING TEST:

Settings No. of Shots:1, Reclaim time :8.00 Sec, Dead Time: 7.0 Sec

| S.No. | Measured Dead Time | Measured Reclaim Time | Remarks |
| --- | --- | --- | --- |
| 1 | 7. 00 | 8. 00 | OK |

Setting reduced for testing purpose

  - CBF (CIRCUIT BREAKER FAILURE-50BF)

Inject for Over Current stage-1 PHLPTOC for pickup time 20msec and adding CBF timer for CBF operate will be Time for I> + time for CBF timer = 40ms + 150ms = 190ms

| Phase | Current (A) |  |  | Operating Time |  |
| --- | --- | --- | --- | --- | --- |
|  | Set | Pickup | Drop-off | Set | OPTD (ms) |
| R | 0.1 | 0.101 | 0.096 | 150 | 194.3 |
| Y |  | 0.101 | 0.096 |  | 192.6 |
| B |  | 0.101 | 0.096 |  | 192.6 |

  - ARC PROTECTION:

Start & Time check

| Phase | Current (A) |  |  | Operating Time |
| --- | --- | --- | --- | --- |
|  | Set | Pickup | Drop-off |  |
| R | 1.2 | 1.203 | 1.152 | 15.4 ms |
| Y |  | 1.198 | 1.151 | 11.6 ms |
| B |  | 1.200 | 1.153 | 17.3 ms |

Sensor Check:

| Sensor Location | Checked |
| --- | --- |
| Breaker Compartment | OK |
| Cable Compartment | OK |
| Busbar Compartment | OK |

| COMPANY | Contractor: HAIF | 3rd : ECO limited | Witness: SEGI |  |
| --- | --- | --- | --- | --- |
| NAME | SHERIF MOHMMED TAHA | AMR AHMED | WITNESSED BY | AHMED SORKATI |
| POSITION | Electrical Engineer | T&C Engineer |  | T&C Engineer |
| ID | 2514359310 | 2501027300 |  | 2571507827 |
| DATE | 18/01/2025 | 18/01/2025 |  | 18/01/2025 |

- FORMULAE FOR IEC/UK & IEEE/US CURVE:

| COMPANY | Contractor: HAIF | 3rd : ECO limited | Witness: SEGI |  |
| --- | --- | --- | --- | --- |
| NAME | SHERIF MOHMMED TAHA | AMR AHMED | WITNESSED BY | AHMED SORKATI |
| POSITION | Electrical Engineer | T&C Engineer |  | T&C Engineer |
| ID | 2514359310 | 2501027300 |  | 2571507827 |
| DATE | 18/01/2025 | 18/01/2025 |  | 18/01/2025 |

- RELAY OUTPUT CONTACTS TEST:

NC = Normally Closed,	NO = Normally Open

| Relay Binary Outputs | Protection Assigned | Output Relay Terminal Numbers | Checked |
| --- | --- | --- | --- |
| X100 - PO1 | PROTECTION OPTD | 6 - 7 (NO) | OK |
| X100 - PO2 | TC1 OPTD | 8 - 9 (NO) | OK |
| X100 - PO3 | TRIP1 CB (TRIP CIRCUIT 1) | 16 - 17 & 18 - 19 (NO) | OK |
| X100 - PO4 | TRIP2 CB (TRIP CIRCUIT 2) | 21 - 22 & 23 - 24 (NO) | OK |
| X100 - SO1 | CBF Operate | 10 - 12 (NO) | OK |
| X100 - SO2 | TC2 OPTD | 13 - 14 (NO) | OK |
| X110 - SO1 | CBF Protection Operate | 14 - 16 (NC) / 14 - 15 (NO) | OK |
| X110 - SO2 | CLOSING FOR A/R | 17 – 19 (NC) / 17 - 18 (NO) | OK |
| X110 - SO3 | BCPU LOCKOUT | 20 - 22 (NC) / 20 - 21 (NO) | OK |
| X110 - SO4 | 50N/51N Operate | 23 - 24 (NO) | OK |
| X100 - IRF | RELAY FAULTY | 3 - 5 (NO) | OK |

- RELAY BINARY INPUT TEST:

| Relay Binary Inputs | Binary Input Relay Terminal | Checked | Function Assigned |
| --- | --- | --- | --- |
| BI-1 | X110: 1, 2 | OK | INTERNAL ARC CABLE |
| BI-2 | X110: 3,4 | OK | AC SUPPLUY FAILURE |
| BI-3 | X110: 5, 6 | OK | CB IN SERVICE |
| BI-4 | X110: 6,7 | OK | CB IN TEST |
| BI-5 | X110: 8, 9 | OK | CB SPRING CHARGED |
| BI-6 | X110: 9, 10 | OK | 86CBF OPTD |
| BI-7 | X110: 11, 12 | OK | LINE E/S CLOSED |
| BI-8 | X110: 12, 13 | OK | DC SUPPLY FAILURE |
| BI-1 | X120: 1, 2 | OK | A/R IN |
| BI-2 | X120: 2, 3 | OK | A/R OUT |
| BI-3 | X120: 2, 4 | OK | LOCAL |
| BI-4 | X120: 5, 6 | OK | REMOTE |
| BI-1 | X130: 1, 2 | OK | CBF INITIATION BCPU SOFT |
| BI-2 | X130: 3,4 | OK | INTERNAL ARC BB |
| BI-3 | X130: 5, 6 | OK | CB CLOSED |
| BI-4 | X130: 7,8 | OK | CB OPENED |

| COMPANY | Contractor: HAIF | 3rd : ECO limited | Witness: SEGI |  |
| --- | --- | --- | --- | --- |
| NAME | SHERIF MOHMMED TAHA | AMR AHMED | WITNESSED BY | AHMED SORKATI |
| POSITION | Electrical Engineer | T&C Engineer |  | T&C Engineer |
| ID | 2514359310 | 2501027300 |  | 2571507827 |
| DATE | 18/01/2025 | 18/01/2025 |  | 18/01/2025 |

- LED’S CHECK:

| LED NO. | FUNCTION ASSIGNED. | LED / INDICATION CHECK |
| --- | --- | --- |
| Led 1 | Phase - R - Start | OK |
| Led 2 | Phase - Y - Start | OK |
| Led 3 | Phase - B - Start | OK |
| Led 4 | Phase - N - Start | OK |
| Led 5 | Over Current Operate | OK |
| Led 6 | Earth Fault Operate | OK |
| Led 7 | Breaker Fail Operate | OK |
| Led 8 | Breaker Fail External Initiation | OK |
| Led 9 | Spare | OK |
| Led 10 | Arc Protection Operate | OK |
| Led 11 | Auto Reclose Shot in Progress | OK |

FOLLOW – S	= Non-Latched mode

FOLLOW – F	= Non-Latched Blinking mode

LATCHED – S	= Latched mode LATCHEDACK – F – S	= Latched Blinking mode

- TEST EQUIPMENT USED:

| Description | Serial Number | Make | Model | Certificate No. | Calibration Due Date |
| --- | --- | --- | --- | --- | --- |
| Relay Test System | 7501728 | Programma | FREJA 300 | 2025/E3254 | 14-Jan-2026 |